## Sheet1
G Panel Modbus Register Mapping
Channel Name | Channel # | Register(s) (Decimal) | Bit | Mask | # of Words
Typical non Bifuel, G-panel unit - Channel # is matched with GenLink DCP
- <Analog_Input_Channels>
OIL TEMPERATURE | 1 | 140 | N/A | N/A | 1
COOLANT TEMPERATURE | 2 | 142 | N/A | N/A | 1
OIL PRESSURE | 3 | 144 | N/A | N/A | 1
GOVERNOR COMMAND | 4 | 146 | N/A | N/A | 1
USER CONFIGURABLE 05 | 5 | 148 | N/A | N/A | 1
USER CONFIGURABLE 06 | 6 | 150 | N/A | N/A | 1
USER CONFIGURABLE 07 | 7 | 152 | N/A | N/A | 1
USER CONFIGURABLE 08 | 8 | 154 | N/A | N/A | 1
USER CONFIGURABLE 09 | 9 | 156 | N/A | N/A | 1
COOLANT LEVEL | 10 | 158 | N/A | N/A | 1
FUEL LEVEL | 11 | 160 | N/A | N/A | 1
AI-1 AUX INPUT 1 | 12 | 162 | N/A | N/A | 1
AI-2 AUX INPUT 2 | 13 | 164 | N/A | N/A | 1
USER CONFIGURABLE 14 | 14 | 166 | N/A | N/A | 1
BAT CHARGE CURRENT | 15 | 168 | N/A | N/A | 1
USER CONFIGURABLE 16 | 16 | 170 | N/A | N/A | 1
USER CONFIGURABLE 17 | 17 | 172 | N/A | N/A | 1
BATTERY VOLTAGE | 18 | 174 | N/A | N/A | 1
BUS CURRENT PHASE A | 19 | 176 | N/A | N/A | 1
BUS CURRENT PHASE B | 20 | 178 | N/A | N/A | 1
BUS CURRENT PHASE C | 21 | 180 | N/A | N/A | 1
BUS AVERAGE CURRENT | 22 | 182 | N/A | N/A | 1
GEN CURRENT PHASE A | 23 | 184 | N/A | N/A | 1
GEN CURRENT PHASE B | 24 | 186 | N/A | N/A | 1
GEN CURRENT PHASE C | 25 | 188 | N/A | N/A | 1
GEN AVERAGE CURRENT | 26 | 190 | N/A | N/A | 1
BUS VOLT PHASE A-B | 27 | 192 | N/A | N/A | 1
BUS VOLT PHASE B-C | 28 | 194 | N/A | N/A | 1
BUS VOLT PHASE C-A | 29 | 196 | N/A | N/A | 1
BUS AVERAGE VOLTAGE | 30 | 198 | N/A | N/A | 1
GEN VOLT PHASE A-B | 31 | 200 | N/A | N/A | 1
GEN VOLT PHASE B-C | 32 | 202 | N/A | N/A | 1
GEN VOLT PHASE C-A | 33 | 204 | N/A | N/A | 1
GEN AVERAGE VOLTAGE | 34 | 206 | N/A | N/A | 1
GEN TOTAL KW | 35 | 208 | N/A | N/A | 1
BUS TOTAL KW | 36 | 210 | N/A | N/A | 1
GEN TOTAL PF | 37 | 212 | N/A | N/A | 1
BUS TOTAL PF | 38 | 214 | N/A | N/A | 1
GEN FREQUENCY | 39 | 216 | N/A | N/A | 1
BUS FREQUENCY | 40 | 218 | N/A | N/A | 1
ENGINE RPM | 41 | 220 | N/A | N/A | 1
RPM 2 | 42 | 222 | N/A | N/A | 1
RPM 3 | 43 | 224 | N/A | N/A | 1
- <Digital_Input_Channels>
AUTO SWITCH | 1 | 129 | 15 | 0x8000 | N/A
MANUAL SWITCH | 2 | 129 | 14 | 0x4000 | N/A
ALARM ACKNOWLEDGE | 3 | 129 | 13 | 0x2000 | N/A
EMERGENCY STOP | 4 | 129 | 12 | 0x1000 | N/A
REMOTE START | 5 | 129 | 11 | 0x0800 | N/A
BATTERY CHARGER FAIL | 6 | 129 | 10 | 0x0400 | N/A
RUPTURED BASIN | 7 | 129 | 9 | 0x0200 | N/A
USER CONFIGURABLE 08 | 8 | 129 | 8 | 0x0100 | N/A
USER CONFIGURABLE 09 | 9 | 129 | 7 | 0x0080 | N/A
USER CONFIGURABLE 10 | 10 | 129 | 6 | 0x0040 | N/A
STOP DEADBUS CONNECT | 11 | 129 | 5 | 0x0020 | N/A
EXERCISER | 12 | 129 | 4 | 0x0010 | N/A
GEN SWITCH STATUS | 13 | 129 | 3 | 0x0008 | N/A
UTIL SWITCH STATUS | 14 | 129 | 2 | 0x0004 | N/A
SEL TRIP STATUS | 15 | 129 | 1 | 0x0002 | N/A
MCB STATUS | 16 | 129 | 0 | 0x0001 | N/A
PHASE ROTATION VALID | 17 | 130 | 15 | 0x8000 | N/A
USER CONFIGURABLE 18 | 18 | 130 | 14 | 0x4000 | N/A
USER CONFIGURABLE 19 | 19 | 130 | 13 | 0x2000 | N/A
USER CONFIGURABLE 20 | 20 | 130 | 12 | 0x1000 | N/A
USER CONFIGURABLE 21 | 21 | 130 | 11 | 0x0800 | N/A
USER CONFIGURABLE 22 | 22 | 130 | 10 | 0x0400 | N/A
USER CONFIGURABLE 23 | 23 | 130 | 9 | 0x0200 | N/A
USER CONFIGURABLE 24 | 24 | 130 | 8 | 0x0100 | N/A
MODEM SELECTED | 25 | 130 | 7 | 0x0080 | N/A
GENERATOR OVERSPEED | 26 | 130 | 6 | 0x0040 | N/A
DI-1 | 27 | 130 | 5 | 0x0020 | N/A
DI-2 | 28 | 130 | 4 | 0x0010 | N/A
DI-3 / LINE POWER | 29 | 130 | 3 | 0x0008 | N/A
DI-4 / GENERATOR PWR | 30 | 130 | 2 | 0x0004 | N/A
USER CONFIGURABLE 31 | 31 | 130 | 1 | 0x0002 | N/A
USER CONFIGURABLE 32 | 32 | 130 | 0 | 0x0001 | N/A
- <Digital_Output_Functions>
COMMON ALARM | 1 | 131 | 15 | 0x8000 | N/A
COMMON WARNING | 2 | 131 | 14 | 0x4000 | N/A
LO OIL PRESSURE WARN | 3 | 131 | 13 | 0x2000 | N/A
LO OIL PRESSURE ALRM | 4 | 131 | 12 | 0x1000 | N/A
HI COOLANT TEMP WARN | 5 | 131 | 11 | 0x0800 | N/A
HI COOLANT TEMP ALRM | 6 | 131 | 10 | 0x0400 | N/A
LO COOLANT TEMP WARN | 7 | 131 | 9 | 0x0200 | N/A
HI OIL TEMP WARN | 8 | 131 | 8 | 0x0100 | N/A
HI OIL TEMP ALARM | 9 | 131 | 7 | 0x0080 | N/A
LO BATTERY VOLT WARN | 10 | 131 | 6 | 0x0040 | N/A
HI BATTERY VOLT WARN | 11 | 131 | 5 | 0x0020 | N/A
OVERSPEED ALARM | 12 | 131 | 4 | 0x0010 | N/A
UNDERSPEED ALARM | 13 | 131 | 3 | 0x0008 | N/A
OVER VOLTAGE ALARM | 14 | 131 | 2 | 0x0004 | N/A
UNDER VOLTAGE ALARM | 15 | 131 | 1 | 0x0002 | N/A
OVER FREQUENCY ALARM | 16 | 131 | 0 | 0x0001 | N/A
UNDER FREQUENCY ALRM | 17 | 132 | 15 | 0x8000 | N/A
HI FUEL ALARM | 18 | 132 | 14 | 0x4000 | N/A
LO FUEL WARNING | 19 | 132 | 13 | 0x2000 | N/A
LO FUEL ALARM | 20 | 132 | 12 | 0x1000 | N/A
FAIL TO START ALARM | 21 | 132 | 11 | 0x0800 | N/A
COOLANT LEVEL ALARM | 22 | 132 | 10 | 0x0400 | N/A
RPM SENSOR FAIL ALRM | 23 | 132 | 9 | 0x0200 | N/A
START INHIBIT ALARM | 24 | 132 | 8 | 0x0100 | N/A
ESTOP ALARM | 25 | 132 | 7 | 0x0080 | N/A
OIL PRESS SENSOR FLT | 26 | 132 | 6 | 0x0040 | N/A
OIL TEMP SENSOR FLT | 27 | 132 | 5 | 0x0020 | N/A
COOLANT TEMP SENSOR | 28 | 132 | 4 | 0x0010 | N/A
KNOCK UNIT FAULT | 29 | 132 | 3 | 0x0008 | N/A
KNOCK NOT CALIBRATED | 30 | 132 | 2 | 0x0004 | N/A
XFER SWITCH ERROR AL | 31 | 132 | 1 | 0x0002 | N/A
REVERSE POWER ALARM | 32 | 132 | 0 | 0x0001 | N/A
MCB IS OPEN | 33 | 133 | 15 | 0x8000 | N/A
OIL FILT BLOCKD ALRM | 34 | 133 | 14 | 0x4000 | N/A
AIR FILT BLOCKD ALRM | 35 | 133 | 13 | 0x2000 | N/A
OXYGEN SENSOR FAULT | 36 | 133 | 12 | 0x1000 | N/A
ALTERNATOR PROBLEM | 37 | 133 | 11 | 0x0800 | N/A
GAS PRESSURE WARN | 38 | 133 | 10 | 0x0400 | N/A
EXHAUST TEMP WARNING | 39 | 133 | 9 | 0x0200 | N/A
EXHAUST TEMP ALARM | 40 | 133 | 8 | 0x0100 | N/A
FLAME DETECTION | 41 | 133 | 7 | 0x0080 | N/A
CARBON MONOXIDE ALRM | 42 | 133 | 6 | 0x0040 | N/A
VACUUM SENSOR FAULT | 43 | 133 | 5 | 0x0020 | N/A
CAM MAPPED O P | 44 | 133 | 4 | 0x0010 | N/A
CRANK MAPPED O P | 45 | 133 | 3 | 0x0008 | N/A
GAS FLOW SENSOR FLT | 46 | 133 | 2 | 0x0004 | N/A
GENERATOR IN AUTO | 47 | 133 | 1 | 0x0002 | N/A
GENERATOR IN MANUAL | 48 | 133 | 0 | 0x0001 | N/A
GENERATOR IN OFF | 49 | 134 | 15 | 0x8000 | N/A
ENGINE STOPPED | 50 | 134 | 14 | 0x4000 | N/A
ENGINE STOPPED-ALARM | 51 | 134 | 13 | 0x2000 | N/A
STOPPED READY TO RUN | 52 | 134 | 12 | 0x1000 | N/A
RUNNING | 53 | 134 | 11 | 0x0800 | N/A
READY TO ACCEPT LOAD | 54 | 134 | 10 | 0x0400 | N/A
ALARMS ENABLED | 55 | 134 | 9 | 0x0200 | N/A
IN WARM UP | 56 | 134 | 8 | 0x0100 | N/A
IN COOL DOWN | 57 | 134 | 7 | 0x0080 | N/A
CRANKING | 58 | 134 | 6 | 0x0040 | N/A
VOLTAGE DROPOUT | 59 | 134 | 5 | 0x0020 | N/A
VOLTAGE PICKUP | 60 | 134 | 4 | 0x0010 | N/A
IN LINE INTRRPT DLY | 61 | 134 | 3 | 0x0008 | N/A
IN RETURN toUTIL DLY | 62 | 134 | 2 | 0x0004 | N/A
IN TDN | 63 | 134 | 1 | 0x0002 | N/A
LOAD SHEDDING | 64 | 134 | 0 | 0x0001 | N/A
OUT OF SERVICE | 65 | 135 | 15 | 0x8000 | N/A
NEED SERVICE | 66 | 135 | 14 | 0x4000 | N/A
BATTERY CHARGER FAIL | 67 | 135 | 13 | 0x2000 | N/A
LINE POWER | 68 | 135 | 12 | 0x1000 | N/A
GENERATOR POWER | 69 | 135 | 11 | 0x0800 | N/A
GAS REDUCED - KNOCK | 70 | 135 | 10 | 0x0400 | N/A
ALL ENGINES ON LINE | 71 | 135 | 9 | 0x0200 | N/A
SHUTDOWN GENSET | 72 | 135 | 8 | 0x0100 | N/A
CHECK VOLT PHASE ROT | 73 | 135 | 7 | 0x0080 | N/A
CHECK CURR PHASE ROT | 74 | 135 | 6 | 0x0040 | N/A
ILC ALARM/WARNING 1 | 75 | 135 | 5 | 0x0020 | N/A
ILC ALARM/WARNING 2 | 76 | 135 | 4 | 0x0010 | N/A
GAS SHUTOFF - KNOCK | 77 | 135 | 3 | 0x0008 | N/A
HI INLET MAN TEMP AL | 78 | 135 | 2 | 0x0004 | N/A
HI INLET MAN TEMP WN | 79 | 135 | 1 | 0x0002 | N/A
LO TURBO PRESS - GAS | 80 | 135 | 0 | 0x0001 | N/A
LO TURBO PRESS - DSL | 81 | 136 | 15 | 0x8000 | N/A
LO GAS PRESS SHUTOFF | 82 | 136 | 14 | 0x4000 | N/A
LO GAS PRESS DISABLE | 83 | 136 | 13 | 0x2000 | N/A
HI GAS PRESS DISABLE | 84 | 136 | 12 | 0x1000 | N/A
CAC BYPASS VALVE FLT | 85 | 136 | 11 | 0x0800 | N/A
KNOCK SAMPLE MISSING | 86 | 136 | 10 | 0x0400 | N/A
DISABLE CHECKSYNC BD | 87 | 136 | 9 | 0x0200 | N/A
FAULT RELAY ACTIVE | 88 | 136 | 8 | 0x0100 | N/A
ANNUNCIATOR LIGHT 20 | 89 | 136 | 7 | 0x0080 | N/A
PM-SC COMMS FAILED | 90 | 136 | 6 | 0x0040 | N/A
CHECK IF ILC RUNNING | 91 | 136 | 5 | 0x0020 | N/A
USR CONFIGURABLE 092 | 92 | 136 | 4 | 0x0010 | N/A
USR CONFIGURABLE 093 | 93 | 136 | 3 | 0x0008 | N/A
USR CONFIGURABLE 094 | 94 | 136 | 2 | 0x0004 | N/A
USR CONFIGURABLE 095 | 95 | 136 | 1 | 0x0002 | N/A
USR CONFIGURABLE 096 | 96 | 136 | 0 | 0x0001 | N/A
USR CONFIGURABLE 097 | 97 | 137 | 15 | 0x8000 | N/A
USR CONFIGURABLE 098 | 98 | 137 | 14 | 0x4000 | N/A
USR CONFIGURABLE 099 | 99 | 137 | 13 | 0x2000 | N/A
USR CONFIGURABLE 100 | 100 | 137 | 12 | 0x1000 | N/A
USR CONFIGURABLE 101 | 101 | 137 | 11 | 0x0800 | N/A
USR CONFIGURABLE 102 | 102 | 137 | 10 | 0x0400 | N/A
USR CONFIGURABLE 103 | 103 | 137 | 9 | 0x0200 | N/A
USR CONFIGURABLE 104 | 104 | 137 | 8 | 0x0100 | N/A
USR CONFIGURABLE 105 | 105 | 137 | 7 | 0x0080 | N/A
USR CONFIGURABLE 106 | 106 | 137 | 6 | 0x0040 | N/A
USR CONFIGURABLE 107 | 107 | 137 | 5 | 0x0020 | N/A
USR CONFIGURABLE 108 | 108 | 137 | 4 | 0x0010 | N/A
USR CONFIGURABLE 109 | 109 | 137 | 3 | 0x0008 | N/A
USR CONFIGURABLE 110 | 110 | 137 | 2 | 0x0004 | N/A
USR CONFIGURABLE 111 | 111 | 137 | 1 | 0x0002 | N/A
USR CONFIGURABLE 112 | 112 | 137 | 0 | 0x0001 | N/A
USR CONFIGURABLE 113 | 113 | 138 | 15 | 0x8000 | N/A
USR CONFIGURABLE 114 | 114 | 138 | 14 | 0x4000 | N/A
USR CONFIGURABLE 115 | 115 | 138 | 13 | 0x2000 | N/A
USR CONFIGURABLE 116 | 116 | 138 | 12 | 0x1000 | N/A
USR CONFIGURABLE 117 | 117 | 138 | 11 | 0x0800 | N/A
USR CONFIGURABLE 118 | 118 | 138 | 10 | 0x0400 | N/A
RPM MISSING IN CRANK | 119 | 138 | 9 | 0x0200 | N/A
ON-LINE IN BKUP MODE | 120 | 138 | 8 | 0x0100 | N/A
ENGINE HOURS NOW | N/A | 304 | N/A | N/A | 2